NON-METAL SLUDGE SCRAPER

- Designed and fabricated according to ANSI standard.

All non metal sludge scrapers are designed and fabricated according to ANSI, American

National Standards Institute, standard, and are compatible to existed sludge scrapers

Installed.

- Green materials are selected.

100% recyclable materials are applied. The products completed their duration are not

classified as industrial biomass. Our material is a 100% recyclable.

- No so many spare parts stocked required.

The sprockets which request to purchase so many spare parts in case the axis diameter

of initial and secondary settling tank is differ from each other do not request purchase

so many spare parts in our system, because the diameter of our sprocket is changed

by inserting of a simple adapter. This means that a separate stock of spare parts is not

required.

- No effected by each chain type

Each part of this sludge scraper will be easily compatible to each axis diameter and chain

type such “ pintle “ and “ loop “ chain. The important parts of product are designed to be

replaceable and compatible to different products.

NON-METAL SLUDGE SCRAPER

A. Introduction of main parts

DRIVEN SPROCKET

MAIN CHAIN

IDLE SHAFT & SPROCKET

CONER SHAFT & SPROCKET

FLIGHT & SHOE

NON-METAL SLUDGE SCRAPER

a. Collector chain

Collector chain will be composed of barrel and link as an incorporated type. The collector

chain will be made of high strength PET. The chain will be consisted of main body chain

link and chain pin, fixed pin, and a couple of jaw. When the fixed pin will be inserted

to the inside of chain pin, the couple of jaw will be extended so that the chain pin will

prevent the breakaway of body chain. This structure will make the separation of chain

easily and prevent the damage of sludge scraper from breakaway of chain pin.

Collector chain will be made of polyethylene terephthalate, PET, thermoplastic resin,

so that the collector chain will have a proper endurance and recycling.

The pitch of chain 152.4mm

, as per international standard

of ASME.

Chain pin will be made of

Polyamide and produced

by injection molding.

The attachment will be

assembled with flight will

be a incorporated type,

which will not by separated

to chain and will be made of

polyethylene terephthalate, PET.

Flight will be produced the type of 150mm according to standard required.

| Part No | Pitch mm (in.) | Working Load N (Kgf.) | Average Ultimate Strength N (Kgf.) | Weight (kg./m.) | Barrel |  | Pin |  |  | Side Bar |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | Outside Dia. D (mm.) | Witch W (mm.) | Outside Dia. d (mm.) | Material | Length L (mm.) | Height H (mm.) | Inside Width L1 (mm.) |
|  |  |  |  |  |  |  |  | Poly -amide |  |  |  |
| LKSC- CS720 | 152.4 (6") | 19,610 (2,000) | 39,200 (4,000) | 2.2 | 22.8 | 34 | 22.5 |  | 114 | 56 | 53 |

NON-METAL SLUDGE SCRAPER

b. Flight

The bottom contacting area of flight will be molded by scraper rip for the effective

removing of sludge. A filler block will be inserted between flight and attachment to

exactly set the flight to chain attachment.

.

The flight will be produced by aluminum extruding and the cross section of flight will be

“E” type to receive and feed the sludge load well.  The height and width of flight will be

150mm and 60mm and an anti corrosion coating will be added.

| Part Number | Product | Material | Weight (Kg./m.) | Height (mm.) | Depth (mm.) | Max length (m) |
| --- | --- | --- | --- | --- | --- | --- |
| LKSC – FT100 |  | Aluminium(AL) Or FRP |  | 150 | 60 | 6.0 |

c. Shoe (Return & carry)

Each wearing shoe, 12mm thickness, will be assembled to each flight to prevent the

abrasion of flight during rail and return track running. The wearing shoe will be a proper

material having a enough rust resistance to assure the maximum endurance.

Each flight will be consisted of a set of return shoe and a set of carrier shoe. Return and carrier shoe will

two wearing sides at the both sides and in case a side

will be worn out, the other side will be used. The shoe will be set by stainless steel bolts.

NON-METAL SLUDGE SCRAPER

The return shoe will have a “ L “ type rise foam, 12mm, and will be produced at 76mm of

height, 76mm of width, and 114mm of length. Carrier shoe will be produced at 76mm of

height, 76mm of width, and 140mm of length.

d. Head sprocket and idle sprocket

Head sprocket and idle sprocket will be consisted of a adapter, a herb and a sprocket

body. Head sprocket and idle sprocket will be a half split type and will be tightly

structured by stainless steel bolts. The adapter of sprocket body and herb will be

made of nylon, as half split type.

The assembly of sprocket body will be

conducted by T shape rail which foamed

on herb.

When sprocket herb will be worn out,

it will be easily replaceable by the

separation of sprocket body from the herb.

Head sprocket body will be also

replaceable by idle sprocket body,

because head sprocket body will be

compatible to idle sprocket body.

The adapter in herb will be assembled

by head shaft and non metal key.

A save rim has been molded, as one body and consists with main chain on the around

sprocket tooth, will resist enough to sludge load with abrasion of sprocket at whole

area of main chain during the operation and the sludge load will be uniformly

distributed to the sprocket. The sprocket tooth and herb will be made of thermoplastic

terephthalate (PET).

NON-METAL SLUDGE SCRAPER

The sprocket tooth will be 23 NT and structured as a double life type according to ANSI

standard.

| Part No | Tooths | Chain application | Material | Pitch mm (in.) | Dimension |  | Bolt |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | Outside | Inside |  |  |
|  |  |  |  |  | Dia.D | Dia.D | R. x mm. | Q'ty |
|  |  |  |  |  | (mm.) | (mm.) |  |  |
| LKSC-SP210 | 17 Tooth | Idle- pintle | Polyamide | 152.4 (6") | 421.88 | 276 | M10 x 40L | 8 |
| LKSC-SP310 | 23 Tooth | Head- pintle |  |  | 564.6 |  |  | 8 |
| HUB | 9 ~ 23 Tooth / Pintle, Loop combination |  | Polyester |  | 276 | Ordered manufacturing |  | 4 |

e. Sleeve bearing

The sleeve bearing will be assembled on idle shaft and corner shaft. It supports the

smooth rotation of shaft and sprocket during the rotation of sprocket and releases the

abrasion of sprocket to increase duration. The sleeve bearing, rotating and contacting

directly sprocket, will be made of high density polyethylene which has a high sliding

friction and rust resistance to endure frictional wear during intermittent operation.

For easily replacement from

excess wearing, the sleeve

bearing will be split by 2 parts

and will be fixed to shaft by

stainless bolts.

The sleeve bearing will be

also a thermoplastic material

and the parts over the life

will be recycled.

NON-METAL SLUDGE SCRAPER

h. Driven sprocket

The driven sprocket will be

consisted of sprocket and

body, clamp, and adapter.

The sprocket delivering the

force of driving chain will be

a type of NH78, 40T and

structured by 4 split parts.

It will be made of

high strength nylon.

Sprocket body will be made

of high strength nylon and

structured by 4 split parts for easy replacement without disassembly of shaft.

The clamp will fix body, adapter, and shaft.

The clamp will be a split type and will form

variable shaft diameters to be compatible any

sized shaft diameters.

The whole parts will be made of high

strength thermoplastic material and

any items over the life will be

recycled.

| Part No | Description | Material | Pitch mm (in.) | Dimension |  | Piece | Bolt |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Outside | Inside |  |  |  |
|  |  |  |  | Dia.D | Dia.D |  | R. x mm. | Q'ty |
|  |  |  |  | (mm.) | (mm.) |  |  |  |
| LKSC-SP100-02 | Tooth | Polyamide | 66.27(2.609") | 844.6 | 762 | 4 Piece | M16 x 80L | 16 |
| LKSC-SP100-01 | Body | Polyester |  | 762 | 210 | 4 Piece | M12 x 50L | 8 |
| LKSC-SP100-03 | Clamp | Polyester |  | Inside 210 |  | 2 Piece | M10 x 45L | 4 |

NON-METAL SLUDGE SCRAPER

i. Drive chain

The drive chain which delivers driving force from reducer to driven sprocket will be

manufactured according to NO. 188, the regulation of chain, ASME. The chain will

offset type chain and will be made of high strength thermoplastic nylon resin.

The connection pin of link will be assembled with grinded stainless steel pin and will

endure working loads enough.

- Type : NH-78 Chain

- Pitch : 66.27mm

- Material : High strength thermoplastic

nylon resin

- Working loads : 7,845N (800kgf)

j. Drive sprocket

In case of overloads, drive sprocket will cut off driving power by shear pin. In case of

overload, the sensor pin inserted in the sloped hole of inside sprocket will rise and strike

the limit switch to make alarm. In case of wearing out, it can be re-used by rotating of pin

by 180 ° meaning it has been manufactured two sides symmetry.

Sprocket and boss will be fixed by stainless

snap ring, which do not request any specific

bolt and assembling parts to assure easy

assembly and disassembly.

Shear pin will be made of uniform quality

aluminum and be a V-neck type to exactly

detect the overload.

The sprocket will be made of high

strength thermoplastic nylon or thermoplastic polyacetal. The sensor pin will be made of

engineering plastic, polyacetal, excellent self lubricated.

NON-METAL SLUDGE SCRAPER

To avoid a protrusion of sensor pin by vibration during the operation of sludge scraper,

an O-ring will be inserted in the center of sensor pin.

- Type : NH-78 11NT

- Material : High strength thermoplastic nylon or polyacetal

- Manufacturing method : Injection molding

k. Jaw clutch

The jaw clutch assembled with drive sprocket will cut off or connect the driving force from

each settling tank for easy maintenance of each settling tank. Independent operation of

scraper on each settling tank will be available by jaw clutch application.

In case of overloads, the driving force will be cut off by safety pin. The abnormal cut of

safety pin will be detected by the protrusion of sensor pin. And this will be sensed by limit

switch.

Sprocket and boss will be fixed by stainless

snap ring, which do not request any specific

bolt and assembling parts to assure easy

assembly and disassembly.

Shear pin will be made of uniform quality

aluminum and be a V-neck type to exactly

detect the overload.

The sprocket will be made of high

strength thermoplastic nylon or thermoplastic polyacetal. The sensor pin will be made of

engineering plastic, polyacetal, excellent self lubricated.

To avoid a protrusion of sensor pin by vibration during the operation of sludge scraper,

an O-ring will be inserted in the center of sensor pin.

- Type : NH-78 11NT

- Material : High strength thermoplastic nylon or polyacetal

NON-METAL SLUDGE SCRAPER

- Boss : Nylon

- Jaw clutch : Nylon

- Shear pin : Aluminum

- Sensor pin : Polyacetal

l. Return bracket & wear pin

(1) Return bracket

Return bracket will be consisted of

angle, 75 x 75 x 9t, which will be

adjusted by the length of bracket

body and bottom of settling tank,

and T arm, which connected to

return rail. The length of return

bracket will be adjusted enough

by main body and arm length.

Bracket body will be made of

thermoplastic polypropylene, recyclable. T-arm will made of FRP extruded

or aluminum.

(2) Wear strip

Wear strip will be consisted of return and

carrier wear strip. Wear strip will be made

of HDPE, high density Polyethlene.

Return wear strip with return bracket

will in installed near by water surface

to support flight which will move to the

direction of skim skimmer.

Carrier wear strip will be strictly fixed on

the bottom of settling tank using stainless

corn washer and vinyl cap anchor.